## Notes
DirectLine Data Collection Template - Building Systems and Components
SBCTC Recommended Status Codes:
|  | CODE | Description
|  | ACTIVE | Owned and In Service/Operating
|  | INACTIVE | Not in use, retired, or disposed
|  | DEMO | Demolished
|  | TOS | Temporarily Out of Service/Inactive; Will be returned to service
Process Steps
1 | Collect relevant equipment information (see below for required v. optional data).
2 | Assign Uniformat Level 3 codes (ref. the Uniformat Tab), or request help from Megamation.
3 | Sort by Uniformat code and assign Useful Lives (see Useful Life Table).
4 | Double-check for missing or inconsistent data. | Equipment Condition Codes
5 | Send final spreadsheet to Megamation for a bulk upload. | CODE | Description
|  | 0 | Acceptable - no action required.
Module Table Color Code Key |  | 15 | Moderate - Below acceptable standard; obvious, but minor aesthetic, functional, or operational deficiency.
Green highlighted fields are required for CBPS O&M compliance &/or system-wide standardization |  | 25 | Poor - Well below acceptable standard; requires frequent maintenance, adjustment, reset, etc, or serious aesthetic annoyance.
Blue highlighted fields are extremely valuable for internal O&M processes |  | 35 | Very Poor - Imminent Failure; unable to funcition reliably, requires major operator interventions.
Non-highlighted are useful, but optional |  | 50 | Failed
Date Field Descriptions
Equipment ID | Unique asset code or tag ID within DirectLine | Equipment needs Calibration
Description | Asset description | Check | Description
Parent | Parent class or location | Yes | Should be calibrated regularly (5 year intervals for building energy meters)
Class | Equipment classification | No | No calibration needed.
Building | Campus/building ID (selected from existing building list)
Room #/FLOOR | Room ID (selected from existing room list)
Location | Specific location note(s) - open text
Mfg Name | Manufacturer name
Model | Manufacturer model
Serial Number | Mfr. serial #
Status | Drop down list; see table this page
Warranty end date | Date or year warranty ends
Install date | Date asset was installed
Uniformat 3 # | Uniformat Level 3 classification code (from attached table)
Expected Useful Life | Expected life per attached table (years)
Observed Lifespan | Currently observed or estimated years of use
Notes/Comments | Physical size, capacity, HP, flow rate, etc.
Replacement Cost | Approximate cost to replace
Asset Condition | Drop down list: Current condition rating
Impact of Failure | Effect of failure: Low=1, High=5, etc.
Repair Delay Score | Time or difficulty to repair: Low=1, High=5
Requires Calibration | Drop down list; should be included for building energy submeters.
Use this template to collect necessary asset data and double-check data quality, then send to Megamation for a bulk upload into DirectLine.
The Clean Buildings Performance Standard requires inventories of all building envelope elements, domestic hot water, HVAC, refrigeration, lighting, controls, electric power distribution and on-site generation, and owner-installed energy submeters in buildings complying with the standard.

## DataCollection
COLLEGE NAME | [9 empty] | Dropdown | [7 empty] | Dropdown |  |  | Dropdown
Equipment | Description | Parent | Class | Building | Room #/FLOOR | Location | Mfg Name | Model | Serial Number | Status | Warranty end date | Install date | Uniformat | Expected Useful Life | Observed Lifespan | Notes and Comments | Estimated Replacement Cost | Asset Condition | Impact of Failure | Repair Delay Score | Requires Calibration

## Uniformat
Uniformat Level 3 Codes, by section
Scroll down for additional sub-classifications (Level 4 categories)
A | SUBSTRUCTURE | B | SHELL | C | INTERIORS | D | SERVICES | E | EQPT/FURNISHINGS | F | SPECIAL CONSTRUCTION | G | SITEWORK | Q
A1010 | STANDARD FOUNDATION | B1010 | FLOOR CONSTRUCTION | C1010 | PARTITIONS | D1010 | ELEVATOR AND LIFTS | E1010 | COMMERCIAL EQUIPMENT | F1010 | SPECIAL STRUCTURES | G1O1O | SITE CLEANING | Q1010 | DESIGN TESTING
A1020 | SPECIAL FOUNDATIONS | B1020 | ROOF CONSTRUCTION | C1020 | INTERIOR DOORS | D1020 | ESCALATORS AND MOVING WALKS | E1020 | INSTITUTIONAL EQUIPMENT | F1020 | INTEGRATED CONSTRUCTION | G1020 | SITE DEMOLITION AND RELOCATIONS
A1030 | SLAB ON GRADE | B2010 | EXTERIOR WALLS | C1021 | INTERIOR DOOR SYSTEMS | D1090 | OTHER CONVEYING SYSTEMS | E1030 | VEHICULAR EQUIPMENT | F1030 | SPECIAL CONSTRUCTION SYSTEMS | G1030 | SITE EARTHWORK
A2010 | BASEMENT EXCAVATION | B2020 | EXTERIOR WINDOWS | C1022 | INTERIOR DOOR AND FRAME & HARDWARE | D2010 | PLUMBING FIXTURES | E1090 | OTHER EQUIPMENT | F1040 | SPECIAL FACILITIES | G1040 | HAZARDOUS WASTE REMEDIATION
A2020 | BASEMENT WALLS | B2030 | EXTERIOR DOORS | C1030 | FITTINGS | D2020 | DOMESTIC WATER DISTRIBUTION | E2010 | FIXED FURNISHINGS | F1050 | SPECIAL CONTROLS & INSTRUMENTATION | G2010 | ROADWAYS
|  | B3010 | ROOF COVERINGS | C1040 | INTERIOR WINDOWS-SEALANTS | D2030 | SANITARY WASTE | E2020 | MOVABLE FURNISHINGS | F2010 | BUILDINGS ELEMENTS DEMOLITION | G2020 | PARKING LOTS
|  | B3020 | ROOF OPENING | C2010 | STAIR CONSTRUCTION | D2040 | RAIN WATER DISCHARGE |  |  | F2020 | HAZARDOUS COMPONENTS ABATEMENT | G2030 | PEDESTRIAL PAVING
|  |  |  | C2020 | STAIR FINISHES | D2090 | OTHER PLUMBING SYSTEMS |  |  |  |  | G2040 | SITE DEVELOPMENT
|  |  |  | C3010 | INTERIOR WALL FINISHES | D3000 | MECHANICAL SYSTEMS |  |  |  |  | G2050 | LANDSCAPING
|  |  |  | C3020 | FLOOR FINISHES | D3010 | ENERGY SUPPLY OR CENTRAL PLANT |  |  |  |  | G3010 | WATER SUPPLY
|  |  |  | C3030 | CEILING FINISHES | D3020 | HEAT GENERATING SYSTEMS |  |  |  |  | G3020 | SANITARY SEWER
[6 empty] | D3030 | COOLING GENERATING SYSTEMS |  |  |  |  | G3030 | STORM SEWER
[6 empty] | D3040 | DISTRIBUTION SYSTEMS |  |  |  |  | G3040 | HEATING DISTRIBUTION - OUTSIDE BUILDING (HDOB)
[6 empty] | D3050 | TERMINAL AND PACKAGE UNITS |  |  |  |  | G3050 | COOLING DISTRIBUTION - OUTSIDE BUILDING (CDOB)
[6 empty] | D3060 | CONTROLS AND INSTRUMENTATION |  |  |  |  | G3060 | FUEL DISTRIBUTION
[6 empty] | D3070 | SYSTEMS TESTING AND BALANCING |  |  |  |  | G3090 | OTHER SITE MECNANICAL UTILITIES
[6 empty] | D3090 | OTHER HVAC SYSTEMS AND EQUIPMENT |  |  |  |  | G4010 | ELECTRICAL DISTRIBUTION
[6 empty] | D4010 | SPRINKLERS |  |  |  |  | G4020 | SITE LIGHTINGS
[6 empty] | D4020 | STANDPIPES |  |  |  |  | G4030 | SITE COMMUNICATIONS & SECURITY
[6 empty] | D4030 | FIRE PROTECTION SPECIALTIES |  |  |  |  | G4090 | OTHER SITE ELECTRICAL UTILITIES
[6 empty] | D4090 | OTHER FIRE PROTECTION |  |  |  |  | G9010 | SERVICE & PEDESTRIAN TUNNELS
[6 empty] | D5010 | ELECTRICAL SERVICE & DISTRIBUTION |  |  |  |  | G9090 | OTHER SITE SYSTEMS
[6 empty] | D5020 | LIGHTING AND BRANCH WIRING
[6 empty] | D5030 | COMMUNICATIONS AND SECURITY
[6 empty] | D5090 | OTHER ELECTRICAL SYSTEMS
A | SUBSTRUCTURE | B | SHELL | C | INTERIORS | D | SERVICES | E | EQPT/FURNISHINGS | F | SPECIAL CONSTRUCTION | G | SITEWORK
A1010 | STANDARD FOUNDATION | B1010 | FLOOR CONSTRUCTION | C1010 | PARTITIONS | D1010 | ELEVATOR AND LIFTS | E1010 | COMMERCIAL (OR PROGRAM) EQUIPMENT | F1010 | SPECIAL STRUCTURES | G1010 | SITE CLEANING
| Wall Foundations - General |  | Suspended Basement Floors Construction |  | WALL PARTITIONS - General |  | Elevators - Passenger |  | Commercial equipment - general |  | Special structures - general |  | Site cleaning - general
| Cast in Place Concrete |  | Upper Floors Construction |  | Room Divider |  | Elevators - Freight |  | Commercial Appliances - General |  | Air Supported Structure | G1020 | SITE DEMOLITION & RELOCATIONS
| Precast Concrete Blocks |  | Balconies - General |  | Privacy Curtain |  | Elevators - Lifts |  | Commercial - Refrigerators |  | Pre-Engineered Structures - General |  | Site demolition and relocations - general
| Perimeter Drainage & Insulation |  | Balcony Floors - Wood |  | Toilet Partitions |  | Elevator Components - General |  | Commercial - Stoves |  | Salt Dome Fabric Coverings | G1030 | SITE EARTHWORK
A1020 | SPECIAL FOUNDATIONS |  | Balcony Floors - Concrete |  | Compartments & Cubicles |  | Elevator Components - Control Modernization |  | Commercial - Freezers |  | Salt Dome Structures |  | Site earthwork - general
A1030 | SLAB ON GRADE |  | Balcony Floors - Metal | C1020 | INTERIOR DOORS |  | Elevator Components - Door Operator |  | Commercial - Dishwasher |  | Recycling Tent Fabric Coverings | G1040 | HAZARDOUS WASTE REMEDIATION
| Standard Slab on Grade |  | Balconies - Walls |  | INTERIOR DOORS - General |  | Elevator Components - Door Safety Device |  | Commercial - Oven |  | Recycling Tent Structures |  | Hazardous waste remediation - general
| Structural Slab on Grade |  | Balconies - Railings | C1021 | INTERIOR DOOR SYSTEMS |  | Elevator Components - Phone |  | Commercial - Walk-in Cooler | F1020 | INTEGRATED CONSTRUCTION |  | Environmental Site Assessment - General
| Inclined Slab on Grade |  | Ramps - General |  | Standard Interior Personnel Doors - General |  | Elevator Components - Emergency Power | E1020 | INSTITUTIONAL EQUIPMENT |  | Integrated construction - general |  | ESA - Phase 1
| Trenches, Pits & Bases |  | Ramps - Parking Garage |  | Door Hardware - Locks |  | Elevator Components - Special Emergency Service |  | Institutional Appliances - General |  | Special Purpose Rooms |  | ESA - Phase 2
| Under Slab Drainage & Insulation |  | Ramps - Parking Garage - Topping |  | Door Hardware - Passage Sets |  | Elevator Components - Pit Equipment |  | Institutional - Refrigerators | F1030 | SPECIAL CONSTRUCTION SYSTEMS |  | Removal of Contaminated Soil
A2010 | BASEMENT EXCAVATION |  | Exterior Stairs - General |  | Door Hardware - Closers |  | Elevator Components - Hydraulic Control Valve |  | Institutional - Stoves |  | Special construction systems - general |  | Soil Restoration & Treatment
A2020 | BASEMENT WALLS |  | Exterior Stairs - Concrete | C1022 | INTERIOR DOOR AND FRAME & HARDWARE |  | Elevator Components - Cylinder |  | Institutional - Freezers |  | Sound, Vibration & Seismic Construction |  | Removal of Other Hazardous Materials, Liquids & Structures - General
| Construction |  | Exterior Stairs - Wood |  | Interior Sliding & Folding Door |  | Elevator Components - Machine Room Cooling & Heating |  | Institutional - Dishwasher |  | Radiation Protection |  | Removal of Other Hazardous Materials & Liquids
| Moisture Protection - General |  | Exterior Stairs - Metal |  | Interior Store Fronts/Entrances |  | Elevator Components - Fire Alarm |  | Institutional - Oven |  | Special Security Systems |  | Removal of Container/Structure of G1040
| Garage Wall |  | Exterior Fire Escapes |  | Interior Fire Doors - General |  | Elevator Components - Button Stations |  | Institutional - Walk-in Cooler |  | Vaults | G2010 | ROADWAYS
| Local Repairs |  | Metal Access Ladder |  | Interior Fire Doors - Services/Common Areas |  | Elevator - Cab Finishes |  | Institutional - Washer | F1040 | SPECIAL FACILITIES |  | Roadways - general
| Expansion Joint at Driveway |  | Floor Raceway Systems |  | Interior Fire Doors - Suites |  | Elevator - Code Changes |  | Institutional - Dryer |  | Special facilities - general |  | Roadways - Bases & Sub-Bases
| Below Paved Areas |  | Parking Garage Floors Construction - General |  | Interior Overhead Doors/Grilles |  | Elevator - Barrier Free |  | Institutional Furnishings - General |  | Ice Rinks |  | Roadways - Paving & Surfacing
| Below Landscaped Areas |  | Parking Garage Floors Rehabilitation - General |  | Interior Counter Shutters & Grilles |  | Elevator - Fixtures |  | Institutional - Hoists/Lifts |  | Site Constructed Incinerators |  | Roadways - Curbs, Gutters & Drains
| Insulation |  | Intermediate Slab Restoration |  | Interior Hatches & Access Doors |  | Elevator - Pits |  | Institutional - Bathtubs |  | Underground Storage Tanks - General |  | Roadways - Guardrails & Barriers
| Interior Skin |  | Waterproofing |  | Interior Gates & Rails | D1020 | ESCALATORS AND MOVING WALKS |  | Institutional - Beds |  | Underground Gas Storage Tank |  | Roadways - Painted Lines
| Parking Garage Interior Walls & Columns |  | Crack Repairs | C1030 | FITTINGS |  | All escalators and moving walks - general |  | Institutional - Wheelchairs |  | Underground Diesel Storage Tank |  | Roadways - Markings & Signage
|  |  | Drains |  | FITTINGS - General | D1090 | OTHER CONVEYING SYSTEMS | E1030 | VEHICULAR EQUIPMENT |  | Aboveground Storage Tanks - General |  | Roadways - Vehicular Bridges
|  |  | Paint |  | Storage Shelving |  | Dumbwaiters |  | Vehicular equipment - general |  | Aboveground Gas Storage Tank | G2020 | PARKING LOTS
|  |  | Expansion Joint |  | Built-in Counters & Vanities - General |  | Hoists, Cranes & Stages - General |  | Parking Control Equipment |  | Aboveground Diesel Storage Tank |  | Parking lots - general
|  | B1020 | ROOF CONSTRUCTION |  | Built-In Counters |  | Hoists |  | Loading Dock Equipment | F1050 | SPECIAL CONTROLS & INSTRUMENTATION |  | Parking Lots - Bases & Sub-Bases
|  |  | Flat Roof |  | Stainless Steel Counters |  | Cranes |  | Garage Hoists |  | General controls/instrumentation that don’t fit elsewhere |  | Parking Lots - Paving & Surfacing
|  |  | Pitched Roof |  | Washroom Vanities |  | Swing Stages | E1090 | OTHER EQUIPMENT | F2010 | BUILDING ELEMENTS DEMOLITION |  | Parking Lots - Curbs, Gutters & Drains
|  |  | Canopies |  | Cabinets & Case Work - General |  | Conveyors |  | Other equipment - general | F2020 | HAZARDOUS COMPONENTS ABATEMENT |  | Parking Lots - Parking Booths & Equipment
|  |  | Parking Garage Roof |  | Cabinetry - Common Areas |  | Chutes |  | Maintenance Equipment |  | Hazardous component abatement - general |  | Parking Lots - Markings & Signage
|  | B2010 | EXTERIOR WALLS |  | Cabinetry - Suites | D2010 | PLUMBING FIXTURES |  | Solid Waste Handling Equipment/Structures - General |  | Removal of Hazardous Building Components |  | Parking Lots - Guardrails & Barriers
|  |  | Cast in Place Concrete |  | Other Interior Specialties |  | General plumbing fixtures |  | Garbage Compactors |  | Encapsulation of Hazardous Building Components |  | Parking Lots - Painted Lines
|  |  | Precast Concrete Wall Panels |  | Cubby Storage |  | Water Closets |  | Outside Garbage Enclosures |  | Dilution of Hazardous Materials & Components |  | Parking Lots - Concrete Ramps
|  |  | Concrete Unit Masonry Wall System |  | Lounge Furniture |  | Urinals |  | Food Service Equipment |  | Hazardous Building Materials Surveys (HBS) - General | G2030 | PEDESTRIAL PAVING
|  |  | Clay Brick Masonry Wall System |  | Lockers |  | Lavatories |  | Residential Equipment - General |  | HBS - Asbestos Containing Materials |  | Pedestrian paving - general
|  |  | Stone Veneer Masonry Wall System | C1040 | INTERIOR WINDOWS-SEALANTS |  | Sinks |  | Residential - Refrigerators |  | HBS - Ozone Depleting Substances |  | Pedestrian Paving - Paving & Surfacing
|  |  | Cementitious Cladding System |  | Interior Windows - General |  | Acid Proof Sinks |  | Residential - Stoves |  | HBS - PCBs |  | Pedestrian Paving - Edging
|  |  | Exterior Insulated Finish System Panels (EIFS) |  | Interior Windows - Glazing |  | Bathtubs |  | Residential - Dishwasher |  | HBS - Lead Containing Materials |  | Pedestrian Paving - Exterior Steps
|  |  | Metal Clad Exterior Walls |  | Interior Windows - Sealants |  | Wash Fountains |  | Residential - Freezers |  | HBS - Mercury Containing Materials |  | Pedestrian Paving - Pedestrian Bridges
|  |  | Vinyl Clad Exterior Walls |  | Interior Windows - Window Coverings |  | Showers |  | Residential - Unit Kitchens |  | HBS - Acronitrile / Ethylene Oxide / Off Gassing Substances |  | Pedestrian Paving - Curbs, Gutters & Drains
|  |  | Wood Clad Exterior Walls | C2010 | STAIR CONSTRUCTION |  | Drinking Fountains & Coolers |  | Window Washing Equipment |  | HBS - CFCs |  | Pedestrian Paving - Guardrails & Barriers
|  |  | Stucco Finish |  | INTERIOR STAIR CONSTRUCTION - General |  | Bidets & Other Plumbing Fixtures |  | Athletic, Recreational & Therapeutic Equipment |  | HBS - Mould |  | Pedestrian Paving - Exterior Ramps
|  |  | Masonry - Capping Sills |  | Interior Stairs - Cast in Place Concrete |  | Eye Wash Stations |  | Washers & Dryers - General |  | HBS - Guano |  | Pedestrian Paving - Concrete Pavers
|  |  | Parapets |  | Interior Stairs - Precast Concrete | D2020 | DOMESTIC WATER DISTRIBUTION |  | Washers |  | Hazardous Building Materials Mgmt Plans (HBM) - General | G2040 | SITE DEVELOPMENT
|  |  | Exterior Louvers, Screens & Fencing |  | Interior Stairs - Steel |  | General Domestic water distribution |  | Dryers |  | HBM - Asbestos Containing Materials |  | Site development - general
|  |  | Exterior Sun Control Devices |  | Interior Stairs - Wood |  | Cold Water Service - General |  | Other Specialized Equipment - General |  | HBM - Ozone Depleting Substances |  | Fences & Gates - General
|  |  | Exterior Soffits - General |  | Interior Stairs - Curved |  | Domestic Water Conditioning Equipment |  | Wheelchair Accessible Appliances |  | HBM - PCBs |  | Fencing - Chain Link
|  |  | Soffits - Metal |  | Interior Stairs - Spiral |  | Hot Water Service - General | E2010 | FIXED FURNISHINGS |  | HBM - Lead Containing Materials |  | Fencing - Wood
|  |  | Soffits - Cementitious Boards |  | Interior Stair Handrails & Balustrades |  | Hot Water Tempering Valves |  | General fixed furnishings |  | HBM - Mercury Containing Materials |  | Fencing - Ornamental
|  |  | Soffits - Wood | C2020 | STAIR FINISHES |  | Recirculation Piping | E2020 | MOVABLE FURNISHINGS |  | HBM - Acronitrile / Ethylene Oxide / Off Gassing Substances |  | Fencing - Masonry
|  |  | Soffits - Gypsum Board |  | INTERIOR STAIR FINISHES - General |  | Domestic Water Supply Equipment |  | Movable furnishings - general |  | HBM - CFCs |  | Fencing - Sound Barrier
|  |  | Exterior Sealants/Caulking - Walls/Soffits |  | Interior Stair, Tread & Landing Finishes |  | Plumbing Pipes |  | Plants |  | HBM - Mould |  | Fencing - Aluminum
|  |  | Special Exterior Walls - General |  | Interior Stair Soffit Finishes |  | Domestic Water Equipment - General |  | Lobby Furnishings |  | HBM - Guano |  | Fencing - Galvanized Metal
|  |  | Wood Trim |  | Interior Stair Handrail & Balustrade Finishes |  | Domestic Water Heaters |  | Public Works - Specialized Equipment - General |  | Hazardous Materials Containment (HMC) - General |  | Retaining Walls - General
|  |  | Miscellaneous Painting | C3010 | INTERIOR WALL FINISHES |  | Domestic Water Storage Tanks |  | Salt Brine Production System |  | HMC - PCBs |  | Retaining Walls - Unit Stone
|  | B2020 | EXTERIOR WINDOWS |  | INTERIOR WALL FINISHES - General |  | Domestic Hot Water Boilers |  | Salt Brine Production Pump |  | HMC - Secondary Liquid Containment |  | Retaining Walls - PT Wood
|  |  | Windows - Steel |  | Applied Wallboard Finish |  | Domestic Water Valves |  | Oil & Silt Interceptor Tank System |  | WHMIS - General |  | Retaining Walls - Concrete
|  |  | Windows - Aluminum |  | Concrete Wall Finish |  | Domestic Water Heat Exchanger |  | Fuel Management System |  | Spill Kits |  | Terrace & Perimeter Walls
|  |  | Windows - Wood |  | Wall Plastering | D2030 | SANITARY WASTE | [5 empty] | Signage
|  |  | Windows - Vinyl |  | Tile Wall Finish |  | Sanitary waste - general | [5 empty] | Flagpoles
|  |  | Curtain Walls |  | Terrazzo Wall Finish |  | Waste Piping | [5 empty] | Site Recreational Fixtures/Structures - General
|  |  | Storefronts |  | Painting, Sealing & Staining – Walls |  | Vent Piping | [5 empty] | Site Furnishings
|  |  | Exterior Sealants/Caulking - Windows |  | Wall Coverings - General |  | Floor Drains | [5 empty] | Deck/Gazebo
|  |  | Exterior Sealants/Caulking - Cap Beading |  | Wood Paneling |  | Sanitary Waste Equipment | [5 empty] | Fountains & Watercourses
|  |  | Skylights - General |  | Vinyl Wallpaper |  | Pipe Insulation | [5 empty] | Indoor Swimming Pool
|  | B2030 | EXTERIOR DOORS |  | Wall Paper | D2040 | RAINWATER DISCHARGE | [5 empty] | Outdoor Swimming Pool
|  |  | Doors - Metal |  | Exposed Brick |  | Rain water discharge - general | [5 empty] | Sauna Rooms
|  |  | Doors - Wood |  | Column Coverings |  | Pipe & Fittings | [5 empty] | Jacuzzi/Whirlpool
|  |  | Doors - Storm |  | Acoustic Wall Treatment |  | Roof Drains | [5 empty] | Playing Fields
|  |  | Glazed Doors & Entrances - General | C3020 | FLOOR FINISHES |  | Rainwater Drainage Equipment | [5 empty] | Tennis Courts
|  |  | Doors - Sliding |  | FLOOR FINISHES - General |  | Pipe Insulation | [5 empty] | Squash / Racquet Ball Courts
|  |  | Exterior Sealants/Caulking - Doors |  | Resilient Flooring - General |  | Sump Pumps | [5 empty] | Exercise Room
|  |  | Doors - Revolving |  | RF - Vinyl Tile | D2090 | OTHER PLUMBING SYSTEMS | [5 empty] | Locker Rooms
|  |  | Overhead Doors - General |  | RF - Vinyl Sheet |  | Other plumbing systems - general | [5 empty] | Change Rooms
|  |  | Infrared Detectors |  | RF - Linoleum Tile |  | Acid Waste Systems | [5 empty] | Showers
|  |  | Overhead Doors - Wood |  | RF - Linoleum Sheet |  | Interceptors | [5 empty] | Washrooms
|  |  | Overhead Doors - Metal |  | Carpet - General |  | Pool Piping & Equipment | [5 empty] | Playground Equipment - General
|  |  | Overhead Doors - Service Access |  | Carpet - Sheet |  | Decorative Fountain Piping Devices | [5 empty] | Playground Surfaces
|  |  | Doors - Hatches & Access |  | Carpet - Tile | D3010 | HVAC ENERGY SUPPLY | [5 empty] | Climbing Structure
|  | B3010 | ROOF COVERINGS |  | Wood Flooring - General |  | Energy supply - general | [5 empty] | Swings
|  |  | Inverted - Built-Up Asphalt & Felt Membrane |  | Wood - Standard |  | Oil Supply System | [5 empty] | Slides
|  |  | Inverted - Hot Applied Rubberized Asphalt |  | Wood - Resilient |  | Gas Supply System | [5 empty] | Rocking Equipment
|  |  | Inverted - Modified Bitumen Membrane |  | Wood - Parquet |  | Coal Supply System | [5 empty] | Sandboxes
|  |  | Inverted - Single Ply Membrane |  | Unit Flooring - General |  | Steam Supply System | [5 empty] | Spring Toys
|  |  | Conventional Built-Up Roofing Assembly |  | Flooring - Ceramic |  | Hot Water Supply System |  |  |  |  | G2050 | LANDSCAPING
|  |  | Conventional Single-Ply Roofing Assembly |  | Flooring - Stone |  | Solar Energy System | [5 empty] | Landscaping - general
|  |  | PVC Membrane |  | Flooring - Masonry |  | Wind Energy System | [5 empty] | Fine Grading & Soil Protection
|  |  | EPDM Roofing Assembly |  | Flooring - Porcelain |  | Diesel Supply System | [5 empty] | Erosion Control Measures
|  |  | Unit Tile Roofing - General |  | Flooring - Quarry | D3020 | HVAC HEAT GENERATING SYSTEMS | [5 empty] | Top Soil & Planting Beds
|  |  | Shingles - Asphalt |  | Flooring - Terrazzo |  | Heat generating systems (HVAC) - general | [5 empty] | Seeding & Sodding
|  |  | Shingles - Wood |  | Flooring - Mastic Composition |  | Steam Boilers | [5 empty] | Planting - General
|  |  | Shingles - Slate |  | Flooring - Raised Pedestal |  | Hot Water Boilers - General | [5 empty] | Planting - Trees
|  |  | Shingles - Metal |  | Special Flooring Requirements & Items - General |  | Hot Water Modulating Boilers | [5 empty] | Planting - Shrubs
|  |  | Roofing Tiles |  | Static/Spark Resistant Flooring |  | Reheating Boilers | [5 empty] | Planting - Planters
|  |  | Roofing Panels |  | Slip Resistant Finish |  | Furnaces - General | [5 empty] | Irrigation Systems
|  |  | Copper Roofing |  | Chemical Resistant Finish |  | Furnaces - Gas Warm Air | [5 empty] | Drainage Systems - General
|  |  | Roof Insulation & Fill | C3030 | CEILING FINISHES |  | Furnaces - Oil Warm Air | [5 empty] | Weeping Beds
|  |  | Flashings & Trim |  | CEILING FINISHES - General |  | Furnaces - Electric Warm Air |  |  |  |  | G3010 | WATER SUPPLY
|  |  | Expansion Joints |  | Ceiling - Exposed Concrete Finishes |  | Boiler Room Piping & Specialties | [5 empty] | Water supply - general
|  |  | Eavestroughs, Gutters & Downspouts |  | Ceiling - Gypsum Board Finish |  | Primary Pumps (HVAC Hydronic Systems) | [5 empty] | Potable & Non-Potable Water Systems - General
|  |  | Exterior Sealants/Caulking - Roofing |  | Ceiling - Suspended Acoustic |  | Heating & Cooling Circulation Pumps | [5 empty] | Potable Water Distribution & Storage
|  | B3020 | ROOF OPENING |  | Ceiling - Acoustic Ceiling Tile System |  | Auxiliary Equipment, Equipment & Pipe Insulation - General | [5 empty] | Non-Potable Water Distribution & Storage
|  |  | ROOF OPENINGS - General |  | Ceiling - Suspended Metal |  | Auxiliary Equipment | [5 empty] | Water Well Systems
|  |  | Roof Hatches |  | Ceiling - Wood Panels |  | Equipment & Piping Insulation | [5 empty] | Fire Protection Systems - Piping & Fixtures
|  |  | Gravity Roof Ventilators |  | Ceiling - Gypsum Plaster Finish | D3030 | HVAC COOLING GENERATING SYSTEMS | [5 empty] | Pumping Stations
|  |  | Vents |  | Painting & Staining - Ceilings |  | Cooling generating systems - general | [5 empty] | Water Storage (Tanks, Ponds, Reservoirs, Lagoons …)
|  |  | Roof Safety Anchors |  |  |  | Chillers | [5 empty] | Package Water Treatment Plants
|  |  | Other Roof Penetrations - General |  |  |  | Chillers Conversion | [5 empty] | Environmental
|  |  | Roof Communications Equipment/Structures |  |  |  | Cooling Towers & Evaporative Coolers |  |  |  |  | G3020 | SANITARY SEWER
|  |  | Roof Signage Structures |  |  |  | Refrigeration Equipment - General | [5 empty] | Sanitary sewer - general
|  |  | Roof Drains |  |  |  | Refrigeration - Condensers | [5 empty] | Sanitary Sewer - Piping
[7 empty] | Refrigeration - Compressors | [5 empty] | Sanitary Sewer - Manholes & Cleanouts
[7 empty] | Packaged Air Conditioning (PAC) Units - General | [5 empty] | Septic Disposal System - General
[7 empty] | PAC - Rooftop | [5 empty] | Sanitary Sewer - Septic Tanks/Grease Interceptors
[7 empty] | PAC - Computer Room | [5 empty] | Sanitary Sewer - Drain Fields
[7 empty] | PAC - Unit AC | [5 empty] | Sanitary Sewer - Lift Stations
[7 empty] | Piping & Fittings for cooling units | [5 empty] | Sanitary Sewer - Packaged Water Waste Treatment Plants
[7 empty] | Equipment & Piping Insulation for cooling units | [5 empty] | Sewage Waste Water - Environmental
[6 empty] | D3040 | HVAC DISTRIBUTION SYSTEMS |  |  |  |  | G3030 | STORM SEWER
[7 empty] | Distribution systems - general | [5 empty] | Storm sewer - general
[7 empty] | Air Distribution Systems - General | [5 empty] | Storm Sewer - Piping
[7 empty] | Ducts, Grilles & Dampers | [5 empty] | Storm Sewer - Manholes & Cleanouts
[7 empty] | Make-Up Air Units | [5 empty] | Storm Sewer - Headwalls & Catch Basins
[7 empty] | Air Distribution Fans | [5 empty] | Storm Sewer - Lift Stations
[7 empty] | Pressurization Fans | [5 empty] | Storm Sewer - Retention Ponds
[7 empty] | Steam Heat Distribution Systems | [5 empty] | Storm Sewer - Ditches & Culverts
[7 empty] | Hydronic Distribution Systems - General | [5 empty] | Storm Sewer - Sub-Drainage Systems
[7 empty] | Hydronic Hot Water Distribution Systems | [5 empty] | Storm Sewer - Environmental
[7 empty] | Hydronic Chilled Water Distribution Systems | [5 empty] | Storm Water - Management Facilities
[7 empty] | Hydronic Hot Water & Chilled Water Distribution Systems |  |  |  |  | G3040 | HEATING DISTRIBUTION OUTSIDE BUILDING
[7 empty] | Glycol Heating Distribution Systems | [5 empty] | Heating distribution - outside building (HDOB) - general
[7 empty] | Exhaust Ventilation Distribution Systems - General | [5 empty] | HDOB - Steam Supply
[7 empty] | Exhaust Ventilation - Building | [5 empty] | HDOB - Condensate Return
[7 empty] | Exhaust Ventilation - Garage | [5 empty] | HDOB - Hot Water Supply Systems
[7 empty] | Exhaust Fans | [5 empty] | HDOB - Pumping Stations
[7 empty] | Ceiling Fans |  |  |  |  | G3050 | COOLING DISTRIBUTION OUTSIDE BUILDING
[7 empty] | Auxiliary Equipment for Distribution Systems | [5 empty] | Cooling distribution - outside building (CDOB) - general
[7 empty] | Auxiliary Equipment - Water Pump System | [5 empty] | CDOB - Chilled Water Piping
[7 empty] | Mechanical Insulation for Distribution Systems | [5 empty] | CDOB - Wells for Cooling
[6 empty] | D3050 | HVAC TERMINAL & PACKAGE UNITS | [5 empty] | CDOB - Pumping Stations
[7 empty] | Terminal and package units - general | [5 empty] | CDOB - Cooling Towers on Site
[7 empty] | Terminal Units for Heating & Cooling (TU) - General |  |  |  |  | G3060 | FUEL DISTRIBUTION
[7 empty] | TU - Gas-Fired Heaters | [5 empty] | Fuel distribution - general
[7 empty] | TU - Electric Heater Baseboards | [5 empty] | Fuel Piping
[7 empty] | TU - Electric Heaters Force Flow | [5 empty] | Fuel Equipment
[7 empty] | Terminal Ventilator Units (TVU) - General | [5 empty] | Fuel Storage Tanks
[7 empty] | TVU - Fossil Fuel Fired Heaters | [5 empty] | Fuel Dispensing Stations
[7 empty] | TVU - Electrical Heater Baseboards |  |  |  |  | G3090 | OTHER MECHANICAL UTILITIES
[7 empty] | TVU - Gas-Fired Heaters | [5 empty] | Other site mechanical utilities - general
[7 empty] | Unit Heaters (UH) - General | [5 empty] | Certificate of Approval
[7 empty] | UH- Fossil Fuel Fired Terminal Heaters | [5 empty] | Industrial Waste Systems - General
[7 empty] | UH- Electric Terminal Heaters | [5 empty] | Solid Waste
[7 empty] | UH - Gas-Fired Terminal Heaters | [5 empty] | Liquid Waste
[7 empty] | Fan Coil Terminal Units - General | [5 empty] | POL (Petroleum Oil & Lubricants) Distribution Systems
[7 empty] | Fan Coil Units - Condensing Pans |  |  |  |  | G4010 | ELECTRICAL DISTRIBUTION
[7 empty] | Fan Coil Units - Motors | [5 empty] | Electrical distribution - general
[7 empty] | Fin Tube Terminal Units | [5 empty] | Substations - General
[7 empty] | Unit Air Conditioner- window/through wall, w/wo heating | [5 empty] | Substations Equipment
[7 empty] | Radiant Heater Units (RHU) | [5 empty] | Transformers
[7 empty] | RHU - Gas-Fired | [5 empty] | Overhead Power Distribution
[7 empty] | RHU - Electrical | [5 empty] | Underground Power Distribution
[7 empty] | Package Units (PU) - General |  |  |  |  | G4020 | SITE LIGHTINGS
[7 empty] | PU - Terminal Heat Pumps | [5 empty] | Site lightings - general
[7 empty] | PU - Electric Air Handling Units | [5 empty] | Fixtures & Transformers
[7 empty] | PU - Electric Furnaces | [5 empty] | Poles & Standards
[7 empty] | Other Terminal & Package Units - General | [5 empty] | Underground Wiring Conduits & Duct banks
[7 empty] | Split System Air Conditioning | [5 empty] | Site Lighting Controls
[6 empty] | D3060 | HVAC CONTROLS & INSTRUMENTATION | [5 empty] | Security Lighting Systems
[7 empty] | Controls, instrumentation, monitoring - general | [5 empty] | Light Bollards
[7 empty] | Heat Systems Controls |  |  |  |  | G4030 | SITE COMMUNICATIONS & SECURITY
[7 empty] | Cooling Systems Controls | [5 empty] | Site communications & security - general
[7 empty] | Heating/Cooling Air Handling Control Systems | [5 empty] | Site Telephone Systems
[7 empty] | Exhaust & Ventilating Control Systems | [5 empty] | Site Public Address Systems
[7 empty] | Terminal Unit Control Systems | [5 empty] | Site Detection & Alarm Systems
[7 empty] | Energy Control, Monitoring & Management Systems | [5 empty] | Site Video Surveillance Systems
[7 empty] | Building Automation Systems | [5 empty] | Site Security Access Systems
[7 empty] | Recording Instrumentation |  |  |  |  | G4090 | OTHER SITE ELECTRICAL UTILITIES
[6 empty] | D3070 | HVAC SYSTEMS TESTING & BALANCING | [5 empty] | Other site electrical utilities - general
[7 empty] | General testing & balancing records, manuals, tools, other | [5 empty] | Cathodic Protection - General
[6 empty] | D3090 | OTHER HVAC SYSTEMS & EQUIPMENT | [5 empty] | Cathodic Protection - Parking Garage Slabs
[7 empty] | Other HVAC systems & equipment - general | [5 empty] | Cathodic Protection - Balcony Slabs
[7 empty] | Special Cooling Systems & Devices | [5 empty] | Cathodic Protection - Storage Tanks
[7 empty] | Special Humidity Control | [5 empty] | Site Emergency Power Generation
[7 empty] | Dust Collectors | [5 empty] | Pipe Heat Tracing Cable Systems
[7 empty] | Fume Hoods & Collectors |  |  |  |  | G9010 | SERVICE & PEDESTRIAN TUNNELS
[7 empty] | Air Curtains | [5 empty] | Service & pedestrian tunnels - general
[7 empty] | Air Purifiers | [5 empty] | Service Tunnels
[7 empty] | Industrial Process Ventilation (IVP) Systems - General | [5 empty] | Trench Boxes
[7 empty] | IVP Systems- Paint Spray Booth Ventilation Systems | [5 empty] | Pedestrian Tunnels
[7 empty] | Sensor Systems - General |  |  |  |  | G9090 | OTHER SITE SYSTEMS
[7 empty] | Carbon Monoxide Sensor Systems | [5 empty] | Other site systems - general
[7 empty] | Gas Sensor System | [5 empty] | Mailboxes
[7 empty] | Carbon Dioxide Sensor System | [5 empty] | Barrier Gates
[6 empty] | D4010 | FIRE PROTECTION SPRINKLERS | [5 empty] | Parking Bollards
[7 empty] | Sprinklers - general | [5 empty] | Snow Melting Systems - General
[7 empty] | Sprinkler - Water Supply | [5 empty] | Snow Melting Systems - Hot Water
[7 empty] | Sprinkler - Wet Pipe System | [5 empty] | Snow Melting Systems - Hot Glycol
[7 empty] | Sprinkler - Dry Pipe System | [5 empty] | Snow Melting Systems - Electrical
[6 empty] | D4020 | FIRE PROTECTION STANDPIPES
Standpipes - general
Standpipe & Hose - Water Supply
Standpipe Equipment
Fire Hose Equipment
Pumping Equipment
Fire Pump
Jockey Pump
Standpipe / Valve / Water Supply
[6 empty] | D4030 | FIRE PROTECTION SPECIALTIES
Fire protection specialties - general
Fire Extinguishers
Fire Hose Cabinets (FHC)
Fire Safety Plan
Fire Containment & Egress
[6 empty] | D4090 | OTHER FIRE PROTECTION
Other fire protection - general
Foam Generating Equipment
Clean Extinguishing Agent Systems
Dry Chemical System
Exhaust Hood & Duct Fire Protection
[6 empty] | D5010 | ELECTRICAL SERVICE & DISTRIBUTION
Electrical service & distribution - general
High Tension Services & Distribution
Low Tension Services & Distribution - General
Distribution Panels & Breakers
Transformers
[6 empty] | D5020 | LIGHTING & BRANCH WIRING
Lighting and branch wiring - general
Lighting & BW - Building Interior - General
Lighting & BW - Common Area
Lighting & BW - Suite Fixtures
Lighting & BW - Parking Garage - Interior
Lighting & BW - Exit Lighting
Lighting & BW - Building Exterior - General
Lighting & BW - On Building
Lighting & BW - Parking Area
Lighting & BW - Walkways
Lighting & BW - Parking Garage - Exterior
[6 empty] | D5030 | COMMUNICATION & SECURITY
Communications and security - general
Public Address & Music Systems
Intercommunication & Paging System
Telephone Systems
Call Systems
Television Systems
Clock & Program Systems
Fire Detection & Alarm Systems - General
Fire Alarm Panel
Smoke Detectors
Emergency Bells, Horns, Pulls
Security & Detection Systems - General
Closed Circuit TV System
Card Access System
Card Access Points
Keypad Entry
Door Chimes
[6 empty] | D5090 | OTHER ELECTRICAL SYSTEMS
Other electrical systems - general
Emergency Light Systems
Emergency Power Systems - General
Emergency - Generator Assemblies
Emergency - Battery Equipment
Local Area Networks
Ground-Fault Systems
Emergency Uninterruptible Power System (UPS)
Underfloor Raceways
Lightning Protection Systems
Power Factor Correction

## Useful Life Table
BOMA Preventative Maintenance Manual, Expected Useful Life table
https://deptofcommerce.app.box.com/s/g38qhzhfpbrwlrbsfzc37fjk9dw0rflx
UNIFORMAT |  |  | Expected
3 | Description | Description | Useful Life
B2010 | Exterior walls | Siding: painted wood | 30
B2010 | Exterior walls | Siding: metal | 30
B2010 | Exterior walls | Siding: vinyl | 30
B2010 | Exterior walls | Siding: masonry | 75
B2010 | Exterior walls | Siding: stone | 100
B2010 | Exterior walls | Building Façade: metal curtain wall | 50
B2010 | Exterior walls | Building Façade: glass curtain wall | 50
B2010 | Exterior walls | Building Façade: precast panels | 35
B2010 | Exterior walls | Building Façade: stone veneer | 50
B2010 | Exterior walls | Building Façade: windows (operable or gasketed) | 30
B2030 | Exterior doors | Door hardware: entry lock sets | 7
B2030 | Exterior doors | Door hardware: closures | 7
B2030 | Exterior doors | Door hardware: automatic doors | 5
B3010 | Roofs/roofing | Roofing: 4-ply built up, asphalt, flat, no slope | 18
B3010 | Roofs/roofing | Roofing: 4-ply built up, asphalt, sloped | 25
B3010 | Roofs/roofing | Roofing: 4-ply built up, cold tar | 35
B3010 | Roofs/roofing | Roofing: 4-ply built up, hot-applied rubberized asphalt (membrane) | 30
B3010 | Roofs/roofing | Roofing: 2-ply modified bitumen (mopped down), flat, no slope | 15
B3010 | Roofs/roofing | Roofing: 2-ply modified bitumen (mopped down), flat, sloped | 20
B3010 | Roofs/roofing | Roofing: 1-ply EPDM, flat, no slope | 15
B3010 | Roofs/roofing | Roofing: 1-ply EPDM, flat, sloped | 20
B3010 | Roofs/roofing | Roofing: 1-ply, thermoplastic (Hypalon, PVC) | 20
B3010 | Roofs/roofing | Roofing: 1-ply, modified Bitumen (touched on), flat, no slope | 10
B3010 | Roofs/roofing | Roofing: 1-ply, modified Bitumen (touched on), sloped | 15
B3010 | Roofs/roofing | Metal Roofing: structural roof panels (pre-finished galvanized steel) | 25
B3010 | Roofs/roofing | Metal Roofing: premanufactured architectural roof panels (prefinished aluminum or galvanized steel) | 25
B3010 | Roofs/roofing | Metal Roofing: Custom Fabricated Standing Seam Roofing (Copper, Lead Coated Copper, Terne Coated Stainless Steel) | 75
B3010 | Roofs/roofing | Metal Roofing: Custom Fabricated Flat Seam (Copper, Lead Coated Copper, Terne Coated Stainless Steel) | 50
B3010 | Roofs/roofing | Asphalt roofing: 15-year | 15
B3010 | Roofs/roofing | Asphalt roofing: 20-year | 20
B3010 | Roofs/roofing | Asphalt roofing: 25-year | 25
B3010 | Roofs/roofing | Asphalt roofing: 30-year | 30
B3010 | Roofs/roofing | Slate roofing: S-1 | 100
B3010 | Roofs/roofing | Slate roofing: S-2 | 75
B3010 | Roofs/roofing | Slate roofing: S-3 | 50
B3010 | Roofs/roofing | Clay/concrete tile roofing | 50
B3010 | Roofs/roofing | Roofing: spray-on polyurethane foam | 10
C3010 | Interior Wall Finishes | Wall coverings: vinyl | 10
C3010 | Interior Wall Finishes | Wall coverings: paint | 5
C3010 | Interior Wall Finishes | Wall coverings: wall paper | 4
C3010 | Interior Wall Finishes | Wall coverings: two-part epoxy | 15
C3010 | Interior Wall Finishes | Wall coverings: fabric | 5
C3010 | Interior Wall Finishes | Wall coverings: wood finish | 15
C3020 | Interior Floor Finishes | Flooring: vinyl tile or sheet | 12
C3020 | Interior Floor Finishes | Flooring: carpet, broad loom | 5
C3020 | Interior Floor Finishes | Flooring: carpet, tiles | 5
C3020 | Interior Floor Finishes | Flooring: carpet, loop pile | 15
C3020 | Interior Floor Finishes | Flooring: epoxy coating | 10
C3020 | Interior Floor Finishes | Flooring: granite | 75
C3020 | Interior Floor Finishes | Flooring: marble | 50
C3020 | Interior Floor Finishes | Flooring: terazzo | 50
C3020 | Interior Floor Finishes | Flooring: hardwood, finished | 10
C3020 | Interior Floor Finishes | Flooring: hardwood substrate | 50
C3020 | Interior Floor Finishes | Flooring: concrete | 50
C3030 | Interior Ceiling Finishes | Ceilings: plaster/dry wall w/ skim coat | 30
C3030 | Interior Ceiling Finishes | Ceilings: suspended, spline system | 20
C3030 | Interior Ceiling Finishes | Ceilings: suspended, lay-in system | 25
C3030 | Interior Ceiling Finishes | Ceilings: suspended, ceiling tiles | 13
C3030 | Interior Ceiling Finishes | Ceilings: metal | 25
C3030 | Interior Ceiling Finishes | Ceilings: wood | 30
D1010 | Elevators/lifts | Elevator: hydraulic, underground cylinder, dry location | 15
D1010 | Elevators/lifts | Elevator: hydraulic, car and pump unit | 35
D1010 | Elevators/lifts | Elevator: traction | 50
D1010 | Elevators/lifts | Elevator: geared traction | 35
D1010 | Elevators/lifts | Elevator: cab interior finish | 10
D1010 | Elevators/lifts | Elevator: carpet | 0.5
D1010 | Elevators/lifts | Controller: electromechanical relay-based | 30
D1010 | Elevators/lifts | Controller: computer-based | 20
D1010 | Elevators/lifts | Elevator door operator: passenger | 20
D1010 | Elevators/lifts | Elevator door operator: freight or service used for carts | 10
D1090 | Interior Conveyances, other | Escalator: dry location, not for mass transit | 40
D1090 | Interior Conveyances, other | Escalator: wet location, and/or for mass transit | 20
D1090 | Interior Conveyances, other | Lift: wheelchair and/or stairway | 25
D2010 | Interior Plumbing Fixtures | Plumbing: flush valves | 12
D2010 | Interior Plumbing Fixtures | Plumbing: commercial faucet | 7
D2010 | Interior Plumbing Fixtures | Plumbing: commercial water closet | 30
D2010 | Interior Plumbing Fixtures | Plumbing: commercial urinal | 30
D2010 | Interior Plumbing Fixtures | Plumbing: commercial sink | 30
D2010 | Interior Plumbing Fixtures | Plumbing: commercial refridgerated drinking fountain | 15
D2020 | Domestic Water systems: interior | Water heater, long warranty: electric, normal use | 15
D2020 | Domestic Water systems: interior | Water heater, long warranty: electric, heavy use or tankless | 10
D2020 | Domestic Water systems: interior | Water heater, long warranty: oil-fired | 18
D2020 | Domestic Water systems: interior | Water heater, long warranty: gas-fired, normal use | 15
D2020 | Domestic Water systems: interior | Water heater, long warranty: gas-fired, heavy use or tankless | 10
D2020 | Domestic Water systems: interior | Water heater, long warranty: solar thermal collector | 20
D2020 | Domestic Water systems: interior | Plumbing pump: base-mounted | 25
D2020 | Domestic Water systems: interior | Plumbing pump: in-line | 15
D2020 | Domestic Water systems: interior | Plumbing pump: sewage ejector | 10
D2020 | Domestic Water systems: interior | Plumbing pump: sump-submerged or pedestal | 10
D2020 | Domestic Water systems: interior | Plumbing pump: well-submerged | 10
D2020 | Domestic Water systems: interior | Plumbing backflow prevention: light duty | 10
D2020 | Domestic Water systems: interior | Plumbing backflow prevention: heavy duty (main service) | 30
D2020 | Domestic Water systems: interior | Domestic Water hot/cold, copper, plastic piping | 30
D2020 | Domestic Water systems: interior | Water softeners | 25
D2030 | Interior Sanitary Waste Water Systems | Domestic waste water piping: PVC or cast iron | 30
D2030 | Interior Sanitary Waste Water Systems | Kitchen waste water piping | 20
D3010 | HVAC Energy Supply Systems | Ground-source heat pump exchange loops | 40
D3010 | HVAC Energy Supply Systems | Gas piping: fuel gas, threaded | 30
D3010 | HVAC Energy Supply Systems | Gas piping: fuel gas, welded | 40
D3010 | HVAC Energy Supply Systems | Gas piping: medical gas supply | 40
D3020 | HVAC Heating Systems | Boiler: hot water, steel water-tube | 30
D3020 | HVAC Heating Systems | Boiler: hot water, steel fire-tube | 30
D3020 | HVAC Heating Systems | Boiler: hot water, cast iron | 30
D3020 | HVAC Heating Systems | Boiler: hot water, electric | 25
D3020 | HVAC Heating Systems | Boiler: hot water, condensing | 15
D3020 | HVAC Heating Systems | Boiler: Steam, cast iron | 30
D3020 | HVAC Heating Systems | Boiler: Steam, steel fire-tube | 25
D3020 | HVAC Heating Systems | Boiler: Steam, steel water-tube | 28
D3020 | HVAC Heating Systems | Burners | 18
D3020 | HVAC Heating Systems | Energy Recovery Air to Air | 12
D3020 | HVAC Heating Systems | Energy Recovery Heat Pipe | 20
D3020 | HVAC Heating Systems | Energy Recovery Water | 12
D3020 | HVAC Heating Systems | Energy Recovery Wheel | 15
D3020 | HVAC Heating Systems | Furnaces: condensing | 15
D3020 | HVAC Heating Systems | Furnaces: gas or oil | 18
D3020 | HVAC Heating Systems | Heat Exchangers, commercial shell & tube: steam to domestic water | 13
D3020 | HVAC Heating Systems | Heat Exchangers, commercial shell & tube: steam to heating water | 20
D3020 | HVAC Heating Systems | Heat Exchangers, commercial shell & tube: water to domestic water | 15
D3020 | HVAC Heating Systems | Heat Exchangers, commercial shell & tube: water to water | 25
D3020 | HVAC Heating Systems | HVAC Coils: electric | 12
D3020 | HVAC Heating Systems | HVAC Coils: water, steam | 20
D3020 | HVAC Heating Systems | Radiant Heater: gas | 18
D3020 | HVAC Heating Systems | Radiant heaters: electric | 10
D3020 | HVAC Heating Systems | Radiant heaters: hot water | 25
D3020 | HVAC Heating Systems | Unit Heaters: gas | 13
D3020 | HVAC Heating Systems | Unit Heaters: electric | 15
D3020 | HVAC Heating Systems | Unit Heaters: hot water or steam | 20
D3030 | HVAC Cooling Systems | Air Conditioner: window unit | 10
D3030 | HVAC Cooling Systems | Air Conditioner: res. single or split package | 15
D3030 | HVAC Cooling Systems | Air Conditioner: commercial | 10
D3030 | HVAC Cooling Systems | Air Conditioner: water-cooled package | 20
D3030 | HVAC Cooling Systems | Air Conditioner: computer room unit | 15
D3030 | HVAC Cooling Systems | Air Conditioner: rooftop, single zone | 18
D3030 | HVAC Cooling Systems | Air Conditioner: rooftop, multizone | 18
D3030 | HVAC Cooling Systems | Air Conditioner: rooftop, VAV | 20
D3030 | HVAC Cooling Systems | Chiller: absorption | 30
D3030 | HVAC Cooling Systems | Chiller: centrifugal | 20
D3030 | HVAC Cooling Systems | Chiller: reciprocating | 20
D3030 | HVAC Cooling Systems | Chiller: screw | 20
D3030 | HVAC Cooling Systems | Chiller: scroll | 15
D3030 | HVAC Cooling Systems | Condensers: air-cooled | 20
D3030 | HVAC Cooling Systems | Condensers: evaporative | 15
D3030 | HVAC Cooling Systems | Cooling tower: ceramic | 35
D3030 | HVAC Cooling Systems | Cooling Tower: fiberglass | 35
D3030 | HVAC Cooling Systems | Cooling Tower: fill media | 15
D3030 | HVAC Cooling Systems | Cooling Tower: galvanized or coated steel | 18
D3030 | HVAC Cooling Systems | Cooling Tower: stainless steel | 25
D3030 | HVAC Cooling Systems | Cooling Tower: wood | 20
D3030 | HVAC Cooling Systems | HVAC Coils: cooling, dehumidifying | 12
D3030 | HVAC Cooling Systems | HVAC Coils: direct expansion | 18
D3030 | HVAC Cooling Systems | Residential packaged or split A/C | 15
D3040 | HVAC Distribution Systems | Air Handler: built-up heavy duty | 30
D3040 | HVAC Distribution Systems | Air Handler: packaged, medium duty | 25
D3040 | HVAC Distribution Systems | Air Handler: severe duty or 100% outside air | 20
D3040 | HVAC Distribution Systems | Air Terminal: Fan coil units | 20
D3040 | HVAC Distribution Systems | Air Terminal: grills, diffusers, registers, heavy gauge, coated | 30
D3040 | HVAC Distribution Systems | Air Terminal: grills, diffusers, registers, perforated or light guage | 15
D3040 | HVAC Distribution Systems | Air Terminal: Induction units | 35
D3040 | HVAC Distribution Systems | Air Terminals: CAV boxes | 25
D3040 | HVAC Distribution Systems | Air Terminals: Double duct boxes | 25
D3040 | HVAC Distribution Systems | Air Terminals: Fan power VAV boxes | 17
D3040 | HVAC Distribution Systems | Air Terminals: Variable volume temperature boxes | 15
D3040 | HVAC Distribution Systems | Air Terminals: VAV boxes, cooling only | 25
D3040 | HVAC Distribution Systems | Dampers: fixed or fusible link | 30
D3040 | HVAC Distribution Systems | Dampers: operable or automatic | 20
D3040 | HVAC Distribution Systems | Ductwork: fiberglass | 15
D3040 | HVAC Distribution Systems | Ductwork: flexible round | 10
D3040 | HVAC Distribution Systems | Ductwork: galvanized steel, aluminum, & black iron | 30
D3040 | HVAC Distribution Systems | Fans: axial | 20
D3040 | HVAC Distribution Systems | Fans: centrifugal | 25
D3040 | HVAC Distribution Systems | Fans: propeller | 15
D3040 | HVAC Distribution Systems | Insulation: blanket | 25
D3040 | HVAC Distribution Systems | Insulation: molded | 20
D3040 | HVAC Distribution Systems | Motor starters: in dry, non-corrosive area | 25
D3040 | HVAC Distribution Systems | Motor starters: in wet or corrosive areas | 10
D3040 | HVAC Distribution Systems | Motors: electric, w/ soft start | 25
D3040 | HVAC Distribution Systems | Motors: electric, w/o soft start | 18
D3040 | HVAC Distribution Systems | Heat Exchanger: Plate and Frame | 25
D3040 | HVAC Distribution Systems | HVAC pumps: base-mounted | 25
D3040 | HVAC Distribution Systems | HVAC pumps: condensate | 15
D3040 | HVAC Distribution Systems | HVAC pumps: in-line | 15
D3040 | HVAC Distribution Systems | HVAC pumps: sump-submerged | 10
D3040 | HVAC Distribution Systems | HVAC pumps: well-submerged | 10
D3040 | HVAC Distribution Systems | Reciprocating air compressors | 15
D3040 | HVAC Distribution Systems | Reciprocating Engines: backup service | 20
D3040 | HVAC Distribution Systems | Reciprocating Engines: continuous service | 5
D3040 | HVAC Distribution Systems | Reciprocating Engines: steam turbines | 30
D3040 | HVAC Distribution Systems | Residential Immersion Coil | 25
D3040 | HVAC Distribution Systems | Fan, ventilating: kitchen or other soiled exhaust | 15
D3040 | HVAC Distribution Systems | Fan, ventilating: roof mounted | 20
D3040 | HVAC Distribution Systems | Heating/cooling piping systems: above ground | 30
D3040 | HVAC Distribution Systems | Flue/chimney: metal, incl. breeching | 20
D3040 | HVAC Distribution Systems | Flue/chimney: steel | 30
D3040 | HVAC Distribution Systems | Flue/chimney: masonry | 50
D3040 | HVAC Distribution Systems | Electrical in Dry, Noncorrosive Locations (Except for Equipment Designed to be Outdoors or in Wet Locations): motors | 18
D3040 | HVAC Distribution Systems | Electrical in Dry, Noncorrosive Locations (Except for Equipment Designed to be Outdoors or in Wet Locations): motor control center | 30
D3050 | HVAC Terminal and Package Units | Heat pump: res. air-to-air | 12
D3050 | HVAC Terminal and Package Units | Heat pump: commercial air-to-air | 15
D3050 | HVAC Terminal and Package Units | Heat pump: commercial water-to-air | 18
D3050 | HVAC Terminal and Package Units | Heater: steam or HW, cast iron convector | 50
D3050 | HVAC Terminal and Package Units | Heater: steam or HW fin tube | 15
D3060 | HVAC Controls and Instrumentation | Control Sensors: air flow | 10
D3060 | HVAC Controls and Instrumentation | Control Sensors: humidity, CO2 | 5
D3060 | HVAC Controls and Instrumentation | Control Sensors: temperature | 20
D3060 | HVAC Controls and Instrumentation | Control Sensors: water flow | 5
D3060 | HVAC Controls and Instrumentation | Controls: computer front end | 15
D3060 | HVAC Controls and Instrumentation | Controls: electric | 20
D3060 | HVAC Controls and Instrumentation | Controls: electronic | 20
D3060 | HVAC Controls and Instrumentation | Controls: pneumatic | 18
D3060 | HVAC Controls and Instrumentation | Valve Actuators: hydraulic | 15
D3060 | HVAC Controls and Instrumentation | Valve Actuators: motorized electric | 18
D3060 | HVAC Controls and Instrumentation | Valve Actuators: pneumatic | 20
D3060 | HVAC Controls and Instrumentation | Valve Actuators: self-contained | 10
D3090 | HVAC Other Systems and Equipment | Air Washer/Humidifiers: pan, wheel, or wetted element | 8
D3090 | HVAC Other Systems and Equipment | Air Washer/Humidifiers: spray | 12
D3090 | HVAC Other Systems and Equipment | Air Washer/Humidifiers: steam | 15
D4010 | Fire Sprinkler systems | Sprinkler systems: heads | 25
D4010 | Fire Sprinkler systems | Fire pumps: electric motor driven | 25
D4010 | Fire Sprinkler systems | Fire pumps: engine driven | 20
D4010 | Fire Sprinkler systems | Sprinkler systems: piping systems | 40
D4010 | Fire Sprinkler systems | Sprinkler systems: equipment and devices (flow switch, dry pipe valve, etc) | 20
D4090 | Fire Alarm systems | Fire alarm systems: activation devices (pull stations, smoke detectors, etc) | 10
D4090 | Fire Alarm systems | Fire alarm systems: notification devices (AV horn, strobe) | 15
D4090 | Fire Alarm systems | Fire alarm systems: control panels | 15
D4090 | Fire Alarm systems | Fire alarm systems: wiring | 30
D5010 | Building Electrical Svc & Distribution | Electrical in Dry, Noncorrosive Locations (Except for Equipment Designed to be Outdoors or in Wet Locations): transformers, oil-filled | 30
D5010 | Building Electrical Svc & Distribution | Electrical in Dry, Noncorrosive Locations (Except for Equipment Designed to be Outdoors or in Wet Locations): transformers, dry | 30
D5010 | Building Electrical Svc & Distribution | Electrical in Dry, Noncorrosive Locations (Except for Equipment Designed to be Outdoors or in Wet Locations): Automatic transfer switch | 25
D5010 | Building Electrical Svc & Distribution | Electrical in Dry, Noncorrosive Locations (Except for Equipment Designed to be Outdoors or in Wet Locations): power panels - light & power distribution boards | 30
D5010 | Building Electrical Svc & Distribution | Electrical in Dry, Noncorrosive Locations (Except for Equipment Designed to be Outdoors or in Wet Locations): switchgear & service entrance equipment | 40
D5010 | Building Electrical Svc & Distribution | Electrical in Dry, Noncorrosive Locations (Except for Equipment Designed to be Outdoors or in Wet Locations): circuit breakers | 30
D5010 | Building Electrical Svc & Distribution | Electrical in Dry, Noncorrosive Locations (Except for Equipment Designed to be Outdoors or in Wet Locations): GFCI switch | 25
D5010 | Building Electrical Svc & Distribution | Electrical in Dry, Noncorrosive Locations (Except for Equipment Designed to be Outdoors or in Wet Locations): wire & cable, < 600V | 40
D5010 | Building Electrical Svc & Distribution | Electrical in Dry, Noncorrosive Locations (Except for Equipment Designed to be Outdoors or in Wet Locations): wire & cable, > 600V | 40
D5010 | Building Electrical Svc & Distribution | Electrical in Dry, Noncorrosive Locations (Except for Equipment Designed to be Outdoors or in Wet Locations): solar PV panels | 20
D5020 | Building Lighting and Branch Wiring | Electrical in Dry, Noncorrosive Locations (Except for Equipment Designed to be Outdoors or in Wet Locations): light fixtures | 20
D5020 | Building Lighting and Branch Wiring | Electrical in Dry, Noncorrosive Locations (Except for Equipment Designed to be Outdoors or in Wet Locations): branch circuit wiring and devices | 30
D5020 | Building Lighting and Branch Wiring | Electrical in Dry, Noncorrosive Locations (Except for Equipment Designed to be Outdoors or in Wet Locations): lighting protection | 40
D5030 | Building Electrical Communications and Security | Security systems: activation devices (access entry, motion sensor, etc) | 10
D5030 | Building Electrical Communications and Security | Security systems: notification devices (horn, dialer) | 15
D5030 | Building Electrical Communications and Security | Security systems: control panels | 15
D5030 | Building Electrical Communications and Security | CCTV: monitors | 53
D5030 | Building Electrical Communications and Security | CCTV: pan and tilt motors | 53
D5030 | Building Electrical Communications and Security | CCTV: cameras | 65
D5030 | Building Electrical Communications and Security | CCTV: computer control | 10
D5090 | Building Electrical Other | Electrical in Dry, Noncorrosive Locations (Except for Equipment Designed to be Outdoors or in Wet Locations): UPS - battery | 10
D5090 | Building Electrical Other | Electrical in Dry, Noncorrosive Locations (Except for Equipment Designed to be Outdoors or in Wet Locations): UPS - rotary | 15
D5090 | Building Electrical Other | Electrical in Dry, Noncorrosive Locations (Except for Equipment Designed to be Outdoors or in Wet Locations): batteries | 5
D5090 | Building Electrical Other | Electrical in Dry, Noncorrosive Locations (Except for Equipment Designed to be Outdoors or in Wet Locations): emergency engine generator set | 20
D5090 | Building Electrical Other | Battery standby power supply | 5
E1020 | NON-PROGRAM INSTITUTIONAL EQUIPMENT/FURNISHINGS | Compressed air piping | 20
E1020 | NON-PROGRAM INSTITUTIONAL EQUIPMENT/FURNISHINGS | Air compressors and vaccuum pumps | 15
F1000 | Special Construction and Structures | Oil storage tank: w/ corrosion protection, above ground | 25
F1000 | Special Construction and Structures | Oil storage tank: w/ corrosion protection, underground | 20
F1000 | Special Construction and Structures | Oil storage tank: w/ corrosion protection, underground, FRP coated steel | 30
G2020 | Site Improvements | Outdoor paved surfaces at grade or topmost level | 30
G2020 | Site Improvements | Outdoor paving with roof, no side wall, covering | 40